## 点表
template_key | standard_code | vendor_name | address_space | address_offset | access | wire_type | byte_order | scale | offset | unit
pcs.p.active_power | active_power | 有功功率 | holding_register | 0 | read | f32 | CDAB | 0.1 | 0 | kW
pcs.q.reactive_power | reactive_power | 无功功率 | holding_register | 2 | read | f32 | CDAB | 0.1 | 0 | kvar
pcs.uab.ac_voltage_ab | ac_voltage_ab | AB 线电压 | holding_register | 4 | read | u16 |  | 0.1 | 0 | V
pcs.ia.ac_current_a | ac_current_a | A 相电流 | holding_register | 5 | read | u16 |  | 0.01 | 0 | A
pcs.f.frequency | frequency | 电网频率 | input_register | 10 | read | u16 |  | 0.01 | 0 | Hz
pcs.dc.dc_voltage | dc_voltage | 直流母线电压 | input_register | 12 | read | u16 |  | 0.1 | 0 | V
pcs.run.run_state | run_state | 运行状态 | discrete_input | 0 | read | bool |  | 1 | 0
pcs.mode.control_mode | control_mode | 控制模式 | input_register | 11 | read | u16 |  | 1 | 0
pcs.fault.fault_active | fault_active | 故障标志 | discrete_input | 1 | read | bool |  | 1 | 0
pcs.start.start | start | 启动 | coil | 0 | write | bool |  | 1 | 0
pcs.stop.stop | stop | 停机 | coil | 1 | write | bool |  | 1 | 0
pcs.setp.set_active_power | set_active_power | 有功功率设定 | holding_register | 20 | write | f32 | CDAB | 1 | 0 | kW
pcs.setq.set_reactive_power | set_reactive_power | 无功功率设定 | holding_register | 22 | write | f32 | CDAB | 1 | 0 | kvar